Copyright 2013 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This Product MasterSpec Section is licensed by ARCOM to Willoughby Industries ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text, and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, ARCOM or The American Institute of Architects (AIA).  Neither AIA nor ARCOM are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user.  A qualified design professional should review and edit the document to suit project requirements.

For more information, contact Willoughby Industries, 5105 W 78th Street, Indianapolis, IN 46268; Phone: (800) 428-4065; Fax: (317) 875-0837; Website: www.willoughby-ind.com; Email: willoughby@willoughby-ind.com.

For information about MasterSpec contact ARCOM at (800) 424-5080 or visit www.MasterSpec.com.

SECTION 224300 - HEALTHCARE PLUMBING FIXTURES

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section includes the following healthcare fixtures and specialties:

Healthcare stainless steel water closets.

Flushometer valves.

Toilet Seats.

Patient care units.

Healthcare shower panels.

Healthcare solid surface shower bases and wall panel kits.

Healthcare shower faucets.

Healthcare bathing units.

Perineal baths.

Bedpan washers.

Bedpan washing equipment.

Clinic sinks.

Plaster sinks.

Stainless steel scrub sinks.

Hose boxes.

Dialysis boxes.

Behavioral healthcare lavatory.

Bariatric healthcare lavatory

Infection control sink.

Hydrotherapy whirlpools.

Morgue equipment.

Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 224100 "Residential Plumbing Fixtures" for residential fixtures for use in healthcare facilities, but not requiring special healthcare fixture attributes.

Section 224213.13 "Commercial Water Closets" for conventional water closets, flushometer valves, carriers, and seats for use healthcare facilities, but not requiring special healthcare fixture attributes.

Section 224213.16 "Commercial Urinals" for urinals for use in healthcare facilities.

Section 224216.13 "Commercial Lavatories" for lavatories for use in healthcare facilities, but not requiring special healthcare fixture attributes.

Section 224216.16 "Commercial Sinks" for sinks for use in healthcare facilities, but not requiring special healthcare fixture attributes.

Section 224223 "Commercial Showers" for showers for use in healthcare facilities, but not requiring special healthcare fixture attributes.

Section 224500 "Emergency Plumbing Fixtures" for emergency showers and eye-wash units.

ACTION SUBMITTALS

Product Data: For each type of product.

Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for fixtures.

Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data: For plumbing fixtures and faucets to include in operation and maintenance manuals.

In addition to items specified in Section 017823 "Operation and Maintenance Data," include the following:

Servicing and adjustments of [flushometer valves] [electronic sensors] [patient care units].

MAINTENANCE MATERIAL SUBMITTALS

Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Faucet Washers and O-Rings: Equal to [10] <Insert number> percent of amount of each type and size installed.

Faucet Cartridges and O-Rings: Equal to [5] <Insert number> percent of amount of each type and size installed.

Flushometer-Valve Repair Kits: Equal to [10] <Insert number> percent of amount of each type installed, but no fewer than [one] [six] <Insert number> of each type.

PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

HEALTHCARE LIGATURE-RESISTANT STAINLESS STEEL WATER CLOSETS

Copy "Healthcare Ligature-Resistant Stainless Steel Water Closets" Paragraph below and re-edit for each type of healthcare water closet required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each healthcare water closet.

Healthcare Ligature-Resistant Stainless Steel Water Closets <Insert drawing designation>: Floor mounted, [top] [back] spud rear access waste outlet [floor] [wall].

For top spud applications, use Willoughby AS-FVC Ligature Resistant flush valve cover.

Basis-of-Design Product: Subject to compliance with requirements, provide Willoughby Industries; [ASETWS-1490-FM] [ASETWS-1490-FM-HC] [ASETF-1490-FM] [ASETF-1490-FM-HC] or a comparable product by one of the following:

Bradley Corp.

<Insert Manufacturer's name>.

Construction:

Standards: ASME A112.19.3/CSA B45.4.

Material: 14 GA type 304 stainless steel.

Type: Siphon jet.

Style: Flushometer valve.

Height: [ADA] [Non ADA].

Rim Contour: Elongated.

Water Consumption: [1.28 gal. (4.8 L)] [1.6 gal. (6 L)] per flush.

Spud Size: NPS 1-1/2 (DN 40).

Coordinate "Flushometer Valve" Subparagraph below with "Flushometer Valves" Article. To require conventional flushometer valves on healthcare water closets, cross-reference Section 224213.13 "Commercial Water Closets."

Flushometer Valve: <Insert flushometer-valve designation>.

Mounting: Floor. Anchor by standard 4-point system. Threaded rods, nuts, and washers furnished. Unit requires chase area for installation and maintenance.

Copy "Healthcare Ligature-Resistant Stainless Steel Water Closets - Front Access" Paragraph below and re-edit for each type of floor-mounted, floor/wall-outlet, healthcare water closet required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each healthcare water closet.

Healthcare Ligature-Resistant Stainless Steel Water Closets - Front Access <Insert drawing designation>: Floor mounted, [top] [back] spud front access waste outlet [floor] [wall].

For top spud applications, use Willoughby AS-FVC Ligature-Resistant flush valve cover.

Basis-of-Design Product: Subject to compliance with requirements, provide Willoughby Industries; [ASETWS-1490-FM-FA] [ASETWS-1490-FM-HC-FA] [ASETF-1490-FM-FA] [ASETF-1490-FM-HC-FA] or a comparable product by one of the following:

Bradley Corporation.

<Insert Manufacturer's name>.

Construction:

Standards: ASME A112.19.3/CSA B45.4.

Material: 14 GA type 304 stainless steel.

Type: Siphon jet.

Style: Flushometer valve.

Height: [ADA] [Non ADA].

Rim Contour: Elongated.

Water Consumption: [1.28 gal. (4.8 L)] [1.6 gal. (6 L)] per flush.

Spud Size: NPS 1-1/2 (DN 40).

Coordinate "Flushometer Valve" Subparagraph below with "Flushometer Valves" Article. To require conventional flushometer valves on healthcare water closets, cross-reference Section 224213.13 "Commercial Water Closets."

Flushometer Valve: <Insert flushometer-valve designation>.

Mounting: Floor. Anchor by standard 4-point system. Threaded rods, nuts, and washers furnished. Unit requires no chase area for installation and maintenance.

Copy "Healthcare Bariatric Stainless Steel Water Closets" Paragraph below and re-edit for each type of floor-mounted, back-outlet healthcare water closet required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each healthcare water closet.

Healthcare Bariatric Stainless Steel Water Closets <Insert drawing designation>: Floor mounted, [floor] [wall] waste outlet, [top] [back] spud [front] [rear] access.

Basis-of-Design Product: Subject to compliance with requirements, provide Willoughby Industries; [BETF-1490-FM-FA] [BETF-1490-FM-FA-10] [BETF-1490-FM-FA-12] [BETW-1490-FM-FA] [BETWS-1490-FM-FA] or a comparable product by one of the following:

Bradley Corporation.

<Insert Manufacturer's name>.

Construction:

Standards: ASME A112.19.23CSA B45.4, CSA Z8000, FGI Healthcare Guidelines.

Material: 14 GA 304 stainless steel.

Type: [Siphon jet] [Blow out].

Style: Flushometer valve.

Height: ADA.

Exterior: White epoxy anti-microbial powder coated.

Bowl Interior: Bead blast stainless steel.

Fixture Load Rating: 1200 lbs (544 kg).

Rim Contour: Elongated [with] [without] bedpan lugs.

Water Consumption: [1.28 gal. (4.8 L)] [1.6 gal. (6 L)] per flush.

Spud Size: NPS 1-1/2 (DN 40).

Coordinate "Flushometer Valve" Subparagraph below with "Flushometer Valves" Article. To require conventional flushometer valves on healthcare water closets, cross-reference Section 224213.13 "Commercial Water Closets".

Flushometer Valve: <Insert flushometer-valve designation>.

Coordinate "Toilet Seat" Subparagraph with "Toilet Seats" Article.

Toilet Seat: Standard (1200 lb capacity).

Wall and floor anchoring hardware to be provided by contractor.

Mounting: Front anchoring through 2 removable 12 inch (305 mm) by 12 inch (305 mm) removable access panels. Fixture provided with four 3/4 inch (19 mm) carrier wall mounting holes and one floor mounted Z-clip.

FLUSHOMETER VALVES

Willoughby Industries does not manufacture Flushometer Valves.

Caution: Consumption of flushometer valves for healthcare stainless steel water closets must match the fixture consumption. Copy "Lever-Handle, Diaphragm Flushometer Valves" Paragraph below and re-edit for each type of lever-handle, diaphragm flushometer valve with bedpan washer required.

Insert letter and number combination number to complete designation. Use these designations on Drawings to identify each flushometer valve.

Lever-Handle, Diaphragm Flushometer Valves <Insert designation>.

Basis-of-Design Product: Subject to compliance with requirements, provide Willoughby Industries; Sloan or a comparable product by one of the following:

Delany Products.

Zurn Industries, LLC.

<Insert Manufacturer's name>.

Standard: ASSE 1037/ASME A112.1037/CSA B125.37.

Maximum Pressure Rating: 125 psig (860 kPa).

Features: Integral check stop, backflow-prevention device, and outlet-tube-mounted bedpan washer.

Material: Brass body with corrosion-resistant components.

Exposed Flushometer-Valve Finish: Chrome plated.

Style: [Exposed] [Concealed].

Consumption: [1.28 gal. (4.8 L)] [1.6 gal. (6 L)] per flush.

Minimum Inlet: NPS 1 (DN 25).

Minimum Outlet: NPS 1-1/2 (DN 40), extended length.

Hydraulic, Diaphragm Flushometer Valves <Insert designation>.

Basis-of-Design Product: Subject to compliance with requirements, provide Willoughby Industries; Sloan or a comparable product by one of the following:

Delany Products.

Zurn Industries, LLC.

<Insert Manufacturer's name>.

Standard: ASSE 1037/ASME A112.1037/CSA B125.37.

Maximum Pressure Rating: 125 psig (860 kPa).

Features: Integral check stop, backflow-prevention device, and outlet-tube-mounted bedpan washer.

Material: Brass body with corrosion-resistant components.

Exposed Flushometer-Valve Finish: Chrome plated.

Style: [Exposed] [Concealed].

Consumption: [1.28 gal. (4.8 L)] [1.6 gal. (6 L)] per flush.

Minimum Inlet: NPS 1 (DN 25).

Minimum Outlet: NPS 1-1/2 (DN 40), extended length.

TOILET SEATS

Willoughby Industries does not manufacture Toilet Seats.

Copy "Toilet Seats" Paragraph below and re-edit for each type of toilet seat required.

Insert letter and number combination to complete designation. Use these designations on Drawings to identify each toilet seat.

Toilet Seats <Insert designation>.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Centoco Manufacturing Corporation.

Church Seats; Bemis Manufacturing Company.

Kohler Co.

Olsonite Seat Co.

Sperzel of Lexington.

Zurn Industries, LLC.

<Insert Manufacturer's name>.

Standard: IAPMO Z124.5.

Material: Plastic with antimicrobial agent.

Type: [Commercial (standard)] [Commercial (heavy duty)].

Shape: Elongated rim, open front.

Hinge: Check.

Hinge Material: Noncorroding metal.

Color: White.

PATIENT CARE UNITS

Copy "Patient Care Units" Paragraph below and re-edit for each type of patient care unit required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each patient care unit.

Patient Care Units <Insert drawing designation>: Factory-fabricated, combination, swivel-away water closet and lavatory healthcare plumbing fixture.

Basis-of-Design Product: Subject to compliance with requirements, provide Willoughby Industries; [WH-1700] [WH-1750] or a comparable product by one of the following:

Bradley Corporation.

<Insert Manufacturer's name>.

Cabinet: Fixed installation with storage space and toilet paper holder.

Material: Fully welded stainless steel full enclosure with solid polymer exterior panels.

For color options, refer to Willoughby Industries website at http://www.willoughby-ind.com/Portals/0/Marketing/Starboard Color Chart.pdf.

Color: <Insert color from manufacturer's full selection>.

Mounting: On floor.

Water Closet: Swivel, floor mounted, [wall] [floor] outlet.

Material: 14 GA type 304 stainless steel.

Orientation: [Left] [Right] hand.

Seal: For outlet.

Flushometer: Concealed flushometer valve with ADA-compliant push-button actuator, wheel handle check stop, and vacuum breaker.

Toilet Seat: White, solid plastic.

Support: Floor plate.

Lavatory Deck: Counter mounted.

Material: Solid-surface.

For color options, refer to Willoughby Industries website at http://www.willoughby-ind.com/Portals/0/Marketing/Aquasurf Color Chart.pdf.

Color:  <Insert color from manufacturer's full selection>.

Faucet: [Gooseneck type with wrist-blade handles] [Gooseneck type with IR activation] <Insert type> complying with ASME A112.18.1/CSA B125.1 and NSF 61 Annex G.

Waste Fittings: Grid drain, with NPS 1-1/4 (DN 32) tailpiece and [NPS 1-1/4 (DN 32)] [NPS 1-1/2 by NPS 1-1/4 (DN 40 by DN 32)] chrome-plated, cast-brass P-trap; tubular-brass waste to wall; and wall flange complying with ASME A112.18.2/CSA B125.2.

Copy "Patient Care Units" Paragraph below and re-edit for each type of factory-fabricated, combination, fixed-position patient care unit required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each patient care unit.

Patient Care Units <Insert drawing designation>: Factory-fabricated, combination, fixed-position water closet and lavatory healthcare fixture.

Basis-of-Design Product: Subject to compliance with requirements, provide Willoughby Industries; [WH-1900] [WH-1950] [WH-2100] [WH-2400] [WH-2600] [WH-2800] or a comparable product by one of the following:

Bradley Corporation.

<Insert Manufacturer's name>.

Cabinet: [Fixed installation] [Swing-away cabinet, for WH-2600] water-closet cover design with storage space and toilet paper holder.

Material: Fully welded stainless steel full enclosure, solid polymer exterior panels.

For color options, refer to Willoughby Industries website at http://www.willoughby-ind.com/Portals/0/Marketing/Starboard Color Chart.pdf.

Color: <Insert color from manufacturer's full selection>.

Mounting: [Floor] [Wall, for WH-2100 and WH-2400].

Water Closet: Floor mounted, [floor] [wall] outlet.

Material: 14 GA type 304 stainless steel.

Orientation: [Left] [Right] hand.

Seal: For outlet.

Flushometer: Concealed flushometer valve with ADA-compliant push-button actuator, wheel handle check stop, and vacuum breaker.

Toilet Seat: White, solid plastic.

Lavatory: Counter mounted.

Material: Solid-surface.

For color options, refer to Willoughby Industries website at http://www.willoughby-ind.com/Portals/0/Marketing/Aquasurf Color Chart.pdf.

Color: <Insert color from manufacturer's full selection>.

Faucet: [Gooseneck type with wrist-blade handles] [Gooseneck type with IR activation] <Insert type> complying with ASME A112.18.1/CSA B125.1 and NSF 61 Annex G.

Waste Fittings: Grid drain, with NPS 1-1/4 (DN 32) tailpiece and [NPS 1-1/4 (DN 32)] [NPS 1-1/4 by NPS 1-1/2 (DN 32 by DN 40)] chrome-plated, cast-brass P-trap; tubular-brass waste to wall; and wall flange complying with ASME A112.18.2/CSA B125.2.

STAINLESS STEEL HEALTHCARE SHOWER PANELS

Copy "Ligature-Resistant Stainless Steel Healthcare Shower Panels" Paragraph below and re-edit for each type of healthcare shower panel required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each stainless steel healthcare shower panel.

Ligature-Resistant Stainless Steel Healthcare Shower Panels <Insert drawing designation>.

Basis-of-Design Product: Subject to compliance with requirements, provide Willoughby Industries; [ASCWSMS] [ASCWSMS-BF-2HD] [ASCWSMS-PBLR] [ASWRS-FA] [ASWRS-BF-2HD] [ASWRS-BF-FA-2HD] or a comparable product by one of the following:

Bradley Corporation.

<Insert Manufacturer's name>.

The following models are ADA compliant: ASCWSMS-BF-2HD; ASWRS-BF-2HD; ASWRS-BF-FA-2HD.

Standard: ASME A112.19.3/CSA B45.4/ADA 2010, ICC A117.1

Construction:

Panel: Fabricated from 16 gauge, type 304 stainless steel with exposed stainless surfaces polished to a #4 satin finish.

Activation Type: [PBH Ligature-resistant pneumatic push-button] [EPBH electronic ligature-resistant push-button] [PZPB Piezo electric push-button] [PBLR Ligature-resistant pressure balancing valve].

Valve: [Single temperature pneumatic metering] [Dual temperature pneumatic metering] [Single temperature electronic metering] [Dual temperature electronic metering] [Pressure balancing] [Thermostatic/pressure balancing] [No valve].

Shower Head: Stainless steel ligature-resistant, hemispherical.

Material: Stainless steel ligature-resistant shower head and pushbutton(s). PBLR Model to have ligature-resistant valve handle.

Soap Dish: [Recessed] [None].

Flow Rate: [2.5 gpm (9.5 L/min.)] [2.0 gpm (7.6 L/min.)] [1.5 gpm (5.7 L/min.)]

HEALTHCARE SOLID SURFACE SHOWER BASES AND WALL PANEL KITS

Copy "Healthcare Solid Surface Shower Bases and Wall Panel Kits" Paragraph below and re-edit for each type of healthcare shower base and wall panel kit required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each healthcare shower base and wall panel kit.

Healthcare Solid Surface Shower Bases ad Wall Panel Kits <Insert drawing designation>.

Basis-of-Design Product: Subject to compliance with requirements, provide Willoughby Industries; [AS-S3462FA] [AS-S3636] [AS-S3840FA] [AS-S36NEO] [AS-S36RND] [AS-S3636ADA] or a comparable product by one of the following:

Bradley Corporation.

<Insert Manufacturer's name>.

The following models are ADA compliant: AS-S3462FA; AS-S3840FA; AS-S3636ADA.

Standard: CSA B45.5/IAPMO Z124, ADA 2010, ICC A117.1

Construction:

Material: Solid surface.

For color options, refer to Willoughby Industries website at http://www.willoughby-ind.com/Portals/0/Marketing/Aquasurf Color Chart.pdf.

Color: <Insert color from manufacturer's full selection>.

Type: [Transfer] [Curbed] [Roll-in] [Neo-Angle] [Round front].

Drain: 2 inch (50 mm) no hub in compliance with ASME A112.18.2/CSA B125.2.

Optional wall panel kit includes 84 inch (2134 mm) tall side walls, overlay battens (as necessary), and corner coves.

Solid Surface Wall panel Kit: [Yes] [No].

Solid Surface Soap/Shampoo Holder: [Yes] [No].

HEALTHCARE SHOWER FAUCETS

Willoughby Industries does not manufacture Healthcare Shower Faucets.

NSF Standard: Comply with NSF 61 Annex G, "Drinking Water System Components - Health Effects," for faucet materials that will be in contact with potable water.

Copy "Healthcare Shower Faucets" Paragraph below and re-edit for each type of pressure-balance mixing valve, healthcare shower faucet required.

Insert letter and number combination to complete designation. Use these designations on Drawings to identify each healthcare shower faucet.

Healthcare Shower Faucets <Insert drawing designation>: Pressure-balance mixing valve.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

American Standard America.

Chicago Faucets; Geberit Company.

FNW; Ferguson Enterprises, Inc.

Kohler Co.

Lawler Manufacturing Company, Inc.

Leonard Valve Company.

Matco-Norca.

Moen Incorporated.

Powers.

Speakman Company.

Zurn Industries, LLC.

<Insert Manufacturer's name>.

Faucet:

Standards: ASME A112.18.1/CSA B125.1 and ASSE 1016.

Body Material: Solid brass.

Finish: Polished chrome plate.

Maximum Flow Rate: [2.5 gpm (9.5 L/min.)] <Insert value> unless otherwise indicated.

Mounting: [Concealed] [Exposed].

Operation: Single-handle, [push-pull] [or] [twist or rotate] control.

Antiscald Device: [Integral with mixing valve] [Separate unit] [Not required].

Check Stops: Check-valve type, integral with or attached to body; on hot- and cold-water-supply connections.

Indicators: For hot and cold water.

Shower Head:

Standard: ASME A112.18.1/CSA B125.1.

Type: [Ball joint with arm and flange] [Without ball joint, but with arm and flange] [Ball joint and head integral with mounting flange] [Integral with mounting flange] [Hand held, slide bar mounted] [Hand held, hook mounted] <Insert type>.

Shower Head Material: Metallic with chrome-plated finish.

Spray Pattern: [Adjustable] [Fixed].

Integral Volume Control: [Not required] [Required].

Retain "Shower-Arm, Flow-Control Fitting" Subparagraph below only if option retained in "Type" Subparagraph above includes arm and flange; otherwise, delete "Shower-Arm, Flow-Control Fitting" Subparagraph below.

Shower-Arm, Flow-Control Fitting: [Not required] [1.5 gpm (5.7 L/min.)] [2.0 gpm (7.6 L/min.)].

Verify availability of feature in "Temperature Indicator" Subparagraph below if required.

Temperature Indicator: [Integral with faucet] [Not required].

Copy "Healthcare Shower Faucets" Paragraph below and re-edit for each type of thermostatic mixing valve, healthcare shower faucet required.

Insert letter and number combination to complete designation. Use these designations on Drawings to identify each healthcare shower faucet.

Healthcare Shower Faucets <Insert drawing designation>: Thermostatic mixing valve.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Chicago Faucets; Geberit Company.

Lawler Manufacturing Company, Inc.

Leonard Valve Company.

Powers.

<Insert Manufacturer's name>.

Faucet:

Standards: ASME A112.18.1/CSA B125.1 and ASSE 1016.

Body Material: Solid brass.

Finish: Polished chrome plate.

Maximum Flow Rate: [2.5 gpm (9.5 L/min.)] <Insert value> unless otherwise indicated.

Mounting: [Concealed] [Exposed].

Operation: Single-handle, [Push-pull] [or] [Twist or Rotate] control.

Antiscald Device: [Integral with mixing valve] [Separate unit] [Not required]

Check Stops: Check-valve type, integral with or attached to body; on hot- and cold-water-supply connections..

Indicators: For hot and cold water.

Shower Head:

Standard: ASME A112.18.1/CSA B125.1.

Type: [Ball joint with arm and flange] [Without ball joint, but with arm and flange] [Ball joint and head integral with mounting flange] [Integral with mounting flange] [Hand held, slide bar mounted] [Hand held, hook mounted] <Insert type>.

Material: Metallic with chrome-plated finish.

Spray Pattern: [Adjustable] [Fixed].

Integral Volume Control: [Not required] [Required].

Retain "Shower-Arm, Flow-Control Fitting" Subparagraph below only if option retained in "Type" Subparagraph above includes arm and flange; otherwise, delete "Shower-Arm, Flow-Control Fitting" Subparagraph below.

Shower-Arm, Flow-Control Fitting: [Not required] [1.5 gpm (5.7 L/min.)] [2.0 gpm (7.6 L/min.)].

Verify availability of feature in "Temperature Indicator" Subparagraph below if required.

Temperature Indicator: [Integral with faucet] [Not required].

HEALTHCARE BATHING UNITS

Willoughby Industries does not manufacture Healthcare Bathing Units.

Caution: Provide one or more floor drains near bathing units.

Copy "Healthcare Bathing Units" Paragraph below and re-edit for each type of side-entry healthcare bathing unit required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each healthcare bathing unit.

Healthcare Bathing Units <Insert drawing designation>: Side-entry[, whirlpool].

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

ARJO, Inc.

Invacare Continuing Care Group.

<Insert Manufacturer's name>.

Fixture: Plastic-tub, institutional bath fixture with integral controls.

Retain "Standard" Subparagraph below if unit has whirlpool.

Standard: UL 1795.

Tub Size: [60 by 30 inches (1524 by 762 mm)] <Insert dimensions>.

Controls: Vacuum breakers on supplies, thermostatic mixing valve, tub fill spout, and hand-held shower head.

Supply Connections: [NPS 3/4 (DN 20)] [NPS 1 (DN 25)] with shutoff valve.

Drain: Manufacturer's standard [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] with tailpiece.

Drain Piping: [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] cast-brass P-trap, waste to wall, and wall flange complying with ASME A112.18.2/CSA B125.2. Include combined drain piping if two drains.

Unit Electrical Characteristics:

Volts: [120] [240] [277] [480] <Insert number>.

Phase(s): [One] [Three].

Hertz: [60] <Insert number>.

Full-Load Amperes: <Insert value>.

Minimum Circuit Ampacity: <Insert value>.

Maximum Overcurrent Protection: <Insert amperage>.

Healthcare bathing units in paragraph below may require additional data for optional features or special applications.

Copy "Healthcare Bathing Units" Paragraph below and re-edit for each type of healthcare bathing unit required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each healthcare bathing unit.

Healthcare Bathing Units <Insert drawing designation>: [Side] [Transfer-lift] [Slide-on] entry, [adjustable] [fixed] height.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

ARJO, Inc.

Clarion Bathware.

Invacare Continuing Care Group.

<Insert Manufacturer's name>.

Fixture: Plastic-tub, institutional bath fixture with integral controls.

Tub Size: [60 by 30 inches (1524 by 762 mm)] <Insert dimensions>.

Controls: Vacuum breakers on supplies, thermostatic mixing valve, tub fill spout, and hand-held shower head.

Supply Connections: [NPS 3/4 (DN 20)] [NPS 1 (DN 25)] with shutoff valve.

Drain: Manufacturer's standard [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] with tailpiece.

Drain Piping: [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] cast-brass P-trap, waste to wall, and wall flange complying with ASME A112.18.2/CSA B125.2. Include combined drain piping if two drains.

Lift System: [Not required] <Insert description>.

Unit Electrical Characteristics:

Volts: [120] [240] [277] [480] <Insert number>.

Phase(s): [One] [Three].

Hertz: [60] <Insert number>.

Full-Load Amperes: <Insert value>.

Minimum Circuit Ampacity: <Insert value>.

Maximum Overcurrent Protection: <Insert amperage>.

Copy "Healthcare Bathing Units" Paragraph below and re-edit for each type of front-entry shower, healthcare bathing unit required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each healthcare bathing unit.

Healthcare Bathing Units <Insert drawing designation>: Front-entry shower.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

ARJO, Inc.

Invacare Continuing Care Group.

<Insert Manufacturer's name>.

Fixture: Plastic-tub, institutional fixture with integral controls.

Cabinet Size: [35 by 41 inches (889 by 1041 mm)] <Insert dimensions>.

Controls: Vacuum breakers on supplies, thermostatic mixing valve, tub fill spout, and hand-held shower head.

Supply Connections: [NPS 3/4 (DN 20)] [NPS 1 (DN 25)] with shutoff valve.

Drain: Manufacturer's standard NPS 2 (DN 50) with tailpiece.

Drain Piping: NPS 2 (DN 50) P-trap, waste to wall, and wall flange complying with ASME A112.18.2/CSA B125.2. Include combined drain piping if two drains.

Unit Electrical Characteristics:

Volts: [120] [240] [277] [480] <Insert number>.

Phase(s): [One] [Three].

Hertz: [60] <Insert number>.

Full-Load Amperes: <Insert value>.

Minimum Circuit Ampacity: <Insert value>.

Maximum Overcurrent Protection: <Insert amperage>.

PERINEAL BATHS

Willoughby Industries does not manufacture Perineal Baths.

Copy "Perineal Baths" Paragraph below and re-edit for each type of pedestal-mounted, vitreous-china perineal bath required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each perineal bath.

Perineal Baths <Insert drawing designation>: Pedestal mounted, vitreous china.

Manufacturers: Subject to compliance with requirements, provide products by the following:

Kohler Co.

<Insert Manufacturer's name>.

Fixture:

Standard: ASME A112.19.2/CSA B45.1.

Color: White.

Drain: NPS 1-1/2 (DN 40) with tailpiece and removable overflow attachment.

Support: Pedestal.

Faucet: Wall-mounting, single-lever-handle, thermostatic mixing valve with concealed supplies and wall-mounting thermometer.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Lawler Manufacturing Company, Inc.

Leonard Valve Company.

Powers.

Symmons Industries, Inc.

<Insert Manufacturer's name>.

Standard: ASME A112.18.1/CSA B125.1.

Material: Brass body and escutcheon.

Flow Rate: Modified to [1.5 gpm (5.7 L/min.)] <Insert value> maximum unless otherwise indicated.

Finish: Polished chrome plate.

Temperature Indicators: Color-coded for hot and cold water.

Exposed Piping: Chrome plated; brass pipe or copper tube.

Supply Connections: NPS 1/2 (DN 15).

Drain Piping: Comply with requirements in "Waste Fittings" Article.

BEDPAN WASHERS

Willoughby Industries does not manufacture Bedpan Washers.

See "Flushometer Valves" Article for flushometer-valve-mounted bedpan washers.

Copy "Bedpan Washers" Paragraph below and re-edit for each type of wall-mounted, compact bedpan washer required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each bedpan washer.

Bedpan Washers <Insert drawing designation>: Wall mounted, compact.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

American Standard America.

Chicago Faucets; Geberit Company.

Kohler Co.

Speakman Company.

T & S Brass and Bronze Works, Inc.

Whitehall Manufacturing.

Zurn Industries, LLC.

<Insert Manufacturer's name>.

Standard: ASME A112.18.1/CSA B125.1.

Hose Assembly: [48-inch- (1220-mm-)] <Insert dimension> long rubber or vinyl hose with self-closing, hand-held spray nozzle, wall bracket, and hook.

Vacuum Breaker: ASSE 1001, atmospheric, wall mounted.

Shutoff Valve: Wall-mounted, [cross-handle] <Insert type> supply stop upstream of vacuum breaker.

Connecting Piping: Concealed.

Finish: Polished chrome-plated finish on exposed metal parts.

Supply Connection: [NPS 1/2 (DN 15)] <Insert size>.

Copy "Bedpan Washers" Paragraph below and re-edit for each type of wall-mounted, bedpan-washer assembly required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each bedpan washer.

Bedpan Washers <Insert drawing designation>: Wall-mounted assembly with [floor] [wall]-mounted, [single-pedal] [double-pedal, hot- and cold-water] foot control.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

American Standard America.

Chicago Faucets; Geberit Company.

Kohler Co.

T & S Brass and Bronze Works, Inc.

Zurn Industries, LLC.

<Insert Manufacturer's name>.

Standard: ASME A112.18.1/CSA B125.1.

Hose: [48-inch- (1220-mm-)] <Insert dimension> long rubber or vinyl hose with self-closing, hand-held spray nozzle, wall bracket, and hook.

Vacuum Breaker: ASSE 1001, atmospheric, wall mounted.

Shutoff Valve: Wall-mounted, [cross-handle] <Insert type> supply stop between foot control and vacuum breaker.

Connecting Piping: Concealed.

Finish: Polished chrome-plated finish on exposed metal parts.

Control Mounting: [Floor] [Wall].

Supply Connection(s): [NPS 1/2 (DN 15)] <Insert size>.

BEDPAN WASHING EQUIPMENT

Willoughby Industries does not manufacture Bedpan Washing Equipment.

Units in this article require separate atmospheric and sanitary vents. Do not connect atmospheric-vent to sanitary-vent piping.

Copy "Bedpan Washers/Sanitizers" Paragraph below and re-edit for each type of bedpan washer/sanitizer required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each bedpan washer/sanitizer.

Bedpan Washers/Sanitizers <Insert drawing designation>: [Recessed] [Wall] mounted.

Manufacturers: Subject to compliance with requirements, provide products by the following:

STERIS Corporation.

<Insert Manufacturer's name>.

Fixture:

Construction: Cast-iron chamber and P-trap waste assembly with spray nozzles and [enameled] [stainless]-steel front panel and cover box.

Controls: Electric, 120-V ac, automatic operation with timer, solenoid valves, and circuit breaker.

Door Mechanism: Foot-pedal operation.

Supply Connections: NPS 1 (DN 25) cold water and NPS 3/8 (DN 10) [hot water] [steam].

Drain Piping: NPS 3 (DN 80) P-trap and soil pipe.

Atmospheric Vent Connection: NPS 2 (DN 50).

Mounting Hardware: Matching fixture-mounting arrangement.

Accessories:

Bedpan Rack(s): [One] [Two] <Insert number>.

Urinal Rack(s): [One] [Two] <Insert number>.

Drain Tray(s): [One] [Two] <Insert number>.

Copy "Bedpan Washers/Disinfectors" Paragraph below and re-edit for each type of bedpan washer/disinfector required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each bedpan washer/disinfector.

Bedpan Washers/Disinfectors <Insert drawing designation>: [Freestanding] [Wall] [Undercounter] mounted.

Manufacturers: Subject to compliance with requirements, provide products by the following:

ARJO, Inc.

<Insert Manufacturer's name>.

Fixture:

Controls: Electric, automatic operation.

Cabinet: Stainless steel.

Wash Chamber: Stainless steel.

Supply Connections: NPS 1/2 (DN 15) cold water and NPS 1/2 (DN 15) hot water.

Drain Piping: NPS 4 (DN 100) P-trap and soil pipe.

Mounting Hardware: Matching fixture-mounting arrangement.

Unit Electrical Characteristics:

Volts: [208] [240] <Insert number>.

Phase(s): [One] [Three].

Hertz: [60] <Insert number>.

Full-Load Amperes: <Insert value>.

Minimum Circuit Ampacity: <Insert value>.

Maximum Overcurrent Protection: <Insert amperage>.

CLINIC SINKS

Willoughby Industries does not manufacture Clinic Sinks.

Copy "Clinic Sinks" Paragraph below and re-edit for each type of wall-mounted clinic sink required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each clinic sink.

Clinic Sinks <Insert drawing designation>: Wall mounted.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

American Standard America.

Crane Plumbing, L.L.C.

Kohler Co.

Zurn Industries, LLC.

<Insert Manufacturer's name>.

Fixture: Back-outlet, vitreous-china, blowout-type, flushing-rim, service sink.

Standard: ASME A112.19.2/CSA B45.1.

Nominal Size: [25 by 20 inches (635 by 510 mm)] <Insert dimensions>.

Outlet Size: NPS 4 (DN 100)[ or NPS 3 (DN 80)].

Color: White.

Rim Guard: Stainless steel, on front.

Coordinate "Flushometer Valve" Subparagraph below with "Flushometer Valves" Article. Use flushometer valve designed for 3.5 gal. (13.2 L) per flush.

Flushometer Valve: <Insert flushometer-valve designation>.

Coordinate "Faucet" Subparagraph below with "Sink Faucets" Article. Use polished, chrome-plated, solid-brass, wall-mounted, service-sink-faucet type in first subparagraph below. Include integral stops in shanks, vacuum breaker, hose-thread outlet, and pail hook.

Faucet: [Not required] <Insert sink-faucet designation>.

Support: ASME A112.61M, Type IV sink carrier.

Copy "Clinic Sinks" Paragraph below and re-edit for each type of floor-mounted clinic sink required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each clinic sink.

Clinic Sinks <Insert drawing designation>: Floor mounted.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

American Standard America.

Crane Plumbing, L.L.C.

Kohler Co.

Zurn Industries, LLC.

<Insert Manufacturer's name>.

Caution: This fixture may require a raised base to attain correct height. Verify with manufacturer.

Fixture: Bottom-outlet, vitreous-china, siphon-jet, flushing-rim, service sink.

Standard: ASME A112.19.2/CSA B45.1.

Nominal Size: [27 by 20 inches (685 by 510 mm)] <Insert dimensions>.

Color: White.

Rim Guards: Stainless steel on front.

Sink Base: [10 inches (254 mm)] <Insert dimension> high; cast terrazzo if required.

Coordinate "Flushometer Valve" Subparagraph below with "Flushometer Valves" Article. Use flushometer valve designed for 3.5 gal. (13.2 L) per flush.

Flushometer Valve: <Insert flushometer-valve designation>.

Coordinate "Faucet" Subparagraph with "Sink Faucets" Article. Use polished, chrome-plated, solid-brass, wall-mounted, service-sink-faucet type in first subparagraph below. Include integral stops in shanks, vacuum breaker, hose-thread outlet, and pail hook.

Faucet: <Insert sink-faucet designation>.

Supply Fittings: Comply with requirements in "Supply Fittings" Article.

PLASTER SINKS

Willoughby Industries does not manufacture Plaster Sinks.

Copy "Plaster Sinks" Paragraph below and re-edit for each type of wall-mounted, vitreous-china plaster sink required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each plaster sink.

Plaster Sinks <Insert drawing designation>: Wall mounted, vitreous china.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

American Standard America.

Crane Plumbing, L.L.C.

Kohler Co.

<Insert Manufacturer's name>.

Fixture:

Standard: ASMA A112.19.2/CSA B45.1.

Type: Utility sink.

Nominal Size: [24 by 22 inches (610 by 560 mm)] [30 by 22 inches (762 by 560 mm)] <Insert dimensions> with back.

Color: White.

Faucet Holes: [One] [Two] in back.

Drain: Grid, NPS 1-1/2 (DN 40)[ with NPS 1-1/2 (DN 40) to NPS 2 (DN 50) adaptor].

Coordinate "Faucet" Subparagraph with "Sink Faucets" Article.

Faucet: <Insert sink-faucet designation>.

Supply Fittings: Comply with requirements in "Supply Fittings" Article.

Drain Piping: [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] chrome-plated brass; 0.045-inch- (1.1-mm-) thick waste to interceptor; interceptor to wall; and wall flange complying with ASME A112.18.2/CSA B125.2.

Plaster Interceptor:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Josam Company.

MIFLB, Inc.

Smith, Jay R. Mfg. Co.

Tyler Pipe; a subsidiary of McWane Inc.

Watts; a Watts Water Technologies company.

Zurn Industries, LLC.

<Insert Manufacturer's name>.

Description: Cast-iron or steel body and removable cover with acid-resistant-enameled interior lining and outside coating; removable, corrosion-resistant metal screens or strainer; and [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] inlet and outlet.

Support: ASME A112.6.1M, Type III sink carrier with white-enameled-steel brackets.

STAINLESS STEEL SCRUB SINKS

Copy "Stainless Steel Scrub Sinks" Paragraph below and re-edit for each type of stainless-steel, wall-mounted scrub sink required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each stainless steel scrub sink.

Stainless Steel Scrub Sinks <Insert drawing designation>: Stainless steel, wall mounted.

Basis-of-Design Product: Subject to compliance with requirements, provide Willoughby Industries; [CWSSS] [EWSSS] [WSSS-ADA] or a comparable product by one of the following:

Just Manufacturing.

Sloan Valve Company.

<Insert Manufacturer's name>.

Construction:

Standard: ASME A112.19.3/CSA B45.4.

Material: Fabricated from heavy gauge, type 304 stainless steel with exposed stainless surfaces polished to a #4 satin finish. Sink interior bead blast finished.

Type: [One-station] [Two station] [Three station].

Drain: Grid, NPS 1-1/2 (DN 40) machined stainless steel with NPS 1-1/2 (DN 40) tailpiece and NPS 1-1/2 (DN 40) FIP slip joint cast brass union "P" trap.

Spout: 6 inch (152 mm) Laminar flow swivel gooseneck.

Body bar and knee operated activation not applicable for WSSS-ADA models.

Activation: [Knee operated] [Infrared hard wired] [Infrared battery operated] [Body bar operated].

Divider Panels: Lexan® divider panel(s).

Above deck mixing valve not available on WSSS-ADA models.

Mixing Valve: [Above deck Thermostatic/Pressure balancing] [Below deck thermostatic].

Soap dispenser not available on WSSS-ADA models.

Knee Operated Soap Dispenser: [Yes] [No].

Waste Fittings: Comply with requirements in "Waste Fittings" Article.

Mounting: "Z" clip with wall anchors.

SINK FAUCETS

Willoughby Industries does not manufacture Sink Faucets.

NSF Standard: Comply with NSF 61 Annex G, "Drinking Water System Components - Health Effects," for faucet-spout materials that will be in contact with potable water.

Copy "Sink Faucets" Paragraph below and re-edit for each type of manual-operation mixing valve, sink faucet required.

Insert letter and number combination to complete drawing designation. Use these designations to identify each sink faucet.

Sink Faucets <Insert drawing designation>: Manual-operation mixing valve.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

American Standard America.

Chicago Faucets; Geberit Company.

Delta Faucet Company.

Elkay Manufacturing Co.

Fisher Manufacturing Co.

GROHE America, Inc.

Just Manufacturing.

Kohler Co.

Moen Incorporated.

Speakman Company.

T & S Brass and Bronze Works, Inc.

Zurn Industries, LLC.

<Insert Manufacturer's name>.

Standard: ASME A112.18.1/CSA B125.1.

Configuration: Hot- and cold-water indicators; coordinate faucet inlets with supplies and fixture hole punchings; coordinate outlet with spout and sink receptor.

Option in "Body Type" Subparagraph below must match fixture hole punching.

Body Type: [Centerset] [Widespread] [Single hole] <Insert type>.

Body Material: Solid brass.

Finish: [Chrome plated] [Polished chrome plate] <Insert finish>.

Maximum Flow Rate: [2.2 gpm (8.3 L/min.)] [2.5 gpm (9.5 L/min.)] <Insert value>.

Retain one of two "Control" subparagraphs below.

Control: [Lever] [Cross, four-arm] [Wrist-blade, 4-inch (102-mm)] [Elbow, 6-inch (152-mm)] <Insert type> handle(s).

Control: [Foot pedal] [Knee action] <Insert type>.

Mounting Type: [Deck, concealed] [Deck, exposed] [Back/wall, exposed] <Insert type>.

Spout Type: [Rigid] [Swivel], [low profile] [gooseneck] <Insert type>.

Retain first option in "Vacuum Breaker" Subparagraph below for sink faucets with hose-thread outlet.

Vacuum Breaker: [Required] [Not required] for hose outlet.

Spout Outlet: [Aerator] [Laminar flow] [Hose thread] [Plain end] [Spray] <Insert type>.

Copy "Sink Faucets" Paragraph below and re-edit for each type of automatic, electronic-sensor-operated mixing valve, sink faucet required.

Insert letter and number combination to complete drawing designation. Use these designations to identify each sink faucet.

Sink Faucets <Insert designation>: Automatic, [battery-powered] [hard-wired], electronic-sensor-operated mixing valve.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

American Standard America.

Chicago Faucets; Geberit Company.

Hydrotek International, Inc.

Kohler Co.

Moen Incorporated.

Sloan Valve Company.

Speakman Company.

T & S Brass and Bronze Works, Inc.

Zurn Industries, LLC.

<Insert Manufacturer's name>.

Standards: ASME A112.18.1/CSA B125.1 and UL 1951.

Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Configuration: Hot- and cold-water indicators; coordinate faucet inlets with supplies and fixture hole punchings; coordinate outlet with spout and fixture receptor.

Option in "Body Type" Subparagraph below must match fixture hole punching.

Body Type: [Centerset] [Widespread] [Single hole] <Insert type>.

Body Material: Solid brass.

Finish: [Polished chrome plate] <Insert finish>.

Maximum Flow Rate: [2.2 gpm (8.3 L/min.)] [2.5 gpm (9.5 L/min.)] <Insert value> unless otherwise indicated.

Mounting Type: [Deck, concealed] [Deck, exposed] [Back/wall, exposed].

Spout Type: [Rigid] [Swivel], [low profile] [gooseneck] <Insert type>.

Retain first option in "Vacuum Breaker" Subparagraph below for sink faucets with hose-thread outlet.

Vacuum Breaker: [Required] [Not required] for hose outlet.

Spout Outlet: [Aerator] [Laminar flow] [Hose thread] [Plain end] [Spray] <Insert type>.

LAMINAR-FLOW, FAUCET-SPOUT OUTLETS

Willoughby Industries does not manufacture Laminar-Flow, Faucet-Spout Outlets.

Retain this article if specifying a laminar-flow, faucet-spout outlet for any sink faucet.

Spout outlets in this article are non-aerating, produce less splashing than conventional faucet spouts, and help reduce bacteria growth.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

AM Conservation Group, Inc.

Chronomite Laboratories, Inc.

NEOPERL, Inc.

<Insert Manufacturer's name>.

Description: Chrome-plated brass, faucet-spout outlet that produces non-aerating, laminar stream. Include external or internal thread that mates with faucet outlet for attachment to faucets where indicated and flow-rate range that includes faucet flow.

NSF Standard: Comply with NSF 61 Annex G, "Drinking Water System Components - Health Effects," for faucet-spout-outlet materials that will be in contact with potable water.

HYDROTHERAPY WHIRLPOOLS

Willoughby Industries does not manufacture Hydrotherapy Whirlpools.

Copy "Hydrotherapy Whirlpools" Paragraph below and re-edit for each type of podiatry, hydrotherapy whirlpool required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each hydrotherapy whirlpool.

Hydrotherapy Whirlpools <Insert drawing designation>: Podiatry.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Ferno Ille.

Whitehall Manufacturing.

<Insert Manufacturer's name>.

Description: Stationary stainless-steel tank for feet and ankles.

Water Capacity: 15 gal. (57 L).

Drain: Waste connection.

Controls.

Thermometer: Control panel or tank mounted.

One electric turbine ejector.

Unit Electrical Characteristics:

Volts: [120] [240] [277] [480] <Insert number>.

Phase(s): [One] [Three].

Hertz: [60] <Insert number>.

Full-Load Amperes: <Insert value>.

Minimum Circuit Ampacity: <Insert value>.

Maximum Overcurrent Protection: <Insert amperage>.

Copy "Hydrotherapy Whirlpools" Paragraph below and re-edit for each type of upper-extremity hydrotherapy whirlpool required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each hydrotherapy whirlpool.

Hydrotherapy Whirlpools <Insert drawing designation>: Upper extremity.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Ferno Ille.

Whitehall Manufacturing.

<Insert Manufacturer's name>.

Description: Stationary, pedestal-mounted, stainless-steel tank for arms, hands, and elbows.

Water Capacity: 25 gal. (95 L).

Drain: Waste connection.

One arm support.

Controls.

Thermometer: Control panel or tank mounted.

One electric turbine ejector.

Unit Electrical Characteristics:

Volts: [120] [240] [277] [480] <Insert number>.

Phase(s): [One] [Three].

Hertz: [60] <Insert number>.

Full-Load Amperes: <Insert value>.

Minimum Circuit Ampacity: <Insert value>.

Maximum Overcurrent Protection: <Insert amperage>.

Copy "Hydrotherapy Whirlpools" Paragraph below and re-edit for each type of high-tank, body hydrotherapy whirlpool required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each hydrotherapy whirlpool.

Hydrotherapy Whirlpools <Insert drawing designation>: High tank, body.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Ferno Ille.

Whitehall Manufacturing.

<Insert Manufacturer's name>.

Description: Stationary stainless-steel tank for legs, hips, and back.

Water Capacity: 105 gal. (397 L).

Drain: Waste connection.

Controls.

Thermometer: Control panel or tank mounted.

One electric turbine ejector.

Unit Electrical Characteristics:

Volts: [120] [240] [277] [480] <Insert number>.

Phases: [One] [Three].

Hertz: [60] <Insert number>.

Full-Load Amperes: <Insert value>.

Minimum Circuit Ampacity: <Insert value>.

Maximum Overcurrent Protection: <Insert amperage>.

Copy "Hydrotherapy Whirlpools" Paragraph below and re-edit for each type of low-tank, body hydrotherapy whirlpool required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each hydrotherapy whirlpool.

Hydrotherapy Whirlpools <Insert drawing designation>: Low tank, body.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Ferno Ille.

Whitehall Manufacturing.

<Insert Manufacturer's name>.

Description: Stationary, extended-length, stainless-steel tank for legs, hips, and lower back.

Water Capacity: 105 gal. (397 L).

Drain: Waste connection.

Controls.

Thermometer: Control panel or tank mounted.

Head rest.

One electric turbine ejector.

Unit Electrical Characteristics:

Volts: [120] [240] [277] [480] <Insert number>.

Phase(s): [One] [Three].

Hertz: [60] <Insert number>.

Full-Load Amperes: <Insert value>.

Minimum Circuit Ampacity: <Insert value>.

Maximum Overcurrent Protection: <Insert amperage>.

Copy "Hydrotherapy Whirlpools" Paragraph below and re-edit for each type of small Hubbard-immersion-tank hydrotherapy whirlpool required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each hydrotherapy whirlpool.

Hydrotherapy Whirlpools <Insert drawing designation>: Small Hubbard immersion tank.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Ferno Ille.

Whitehall Manufacturing.

<Insert Manufacturer's name>.

Description: Stationary butterfly-shaped tank for full-body massage.

Tank Dimensions: [93 by 64 by 22 inches (2362 by 1626 by 560 mm)] <Insert dimensions>.

Overall Height: [34 to 38 inches (864 to 965 mm)] <Insert dimensions>.

Water Capacity: [268 gal. (1014 L)] <Insert value>.

Material: Stainless steel.

Supports: Legs or base.

Controls.

Thermometer: Control panel or tank rim mounted.

Supply: Over-the-rim fill spout.

Drains: Two waste connections.

Electric Turbine Ejectors: Two; one rail mounted on each side.

Thermostatic, mixing-valve assembly.

Unit Electrical Characteristics:

Volts: [120] [240] [277] [480] <Insert number>.

Phase(s): [One] [Three].

Hertz: [60] <Insert number>.

Full-Load Amperes: <Insert value>.

Minimum Circuit Ampacity: <Insert value>.

Maximum Overcurrent Protection: <Insert amperage>.

Insert or delete optional features below to suit Project. Many are available.

Hose and hand-held shower.

Wash-out-hose assembly.

Stretcher lift.

Overhead[ electric] hoist.

<Insert option>.

Copy "Hydrotherapy Whirlpools" Paragraph below and re-edit for each type of medium Hubbard-immersion-tank hydrotherapy whirlpool required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each hydrotherapy whirlpool.

Hydrotherapy Whirlpools <Insert drawing designation>: Medium Hubbard immersion tank.

Manufacturers: Subject to compliance with requirements, provide products by the following:

ARJO, Inc.

<Insert Manufacturer's name>.

Description: Stationary butterfly-shaped tank for full-body massage.

Tank Dimensions: [100 by 73 by 24 inches (2540 by 1854 by 610 mm)] <Insert dimensions>.

Overall Height: [34 to 38 inches (864 to 965 mm)] <Insert dimensions>.

Water Capacity: [377 gal. (1468 L)] <Insert value>.

Material: Stainless steel.

Supports: Legs or base.

Controls.

Thermometer: Control panel or tank rim mounted.

Supply: Over-the-rim fill spout.

Drain: One waste connection.

Electric Turbine Ejector: One; panel mounted.

Thermostatic, mixing-valve assembly.

Unit Electrical Characteristics:

Volts: [120] [240] [277] [480] <Insert number>.

Phase(s): [One] [Three].

Hertz: [60] <Insert number>.

Full-Load Amperes: <Insert value>.

Minimum Circuit Ampacity: <Insert value>.

Maximum Overcurrent Protection: <Insert amperage>.

Insert or delete optional features below to suit Project. Many are available.

Hose and hand-held shower.

Wash-out-hose assembly.

Stretcher lift.

Overhead[ electric] hoist.

<Insert option>.

Copy "Hydrotherapy Whirlpools" Paragraph below and re-edit for each type of large Hubbard-immersion-tank hydrotherapy whirlpool required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each hydrotherapy whirlpool.

Hydrotherapy Whirlpools <Insert drawing designation>: Large Hubbard immersion tank.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Ferno Ille.

Whitehall Manufacturing.

<Insert Manufacturer's name>.

Description: Stationary butterfly-shaped tank for full-body massage.

Tank Dimensions: [106 by 77 by 22 inches (2692 by 1956 by 560 mm)] <Insert dimensions>.

Overall Height: [34 inches (864 mm)] <Insert dimension>.

Water Capacity: [425 gal. (1609 L)] <Insert value>.

Material: Stainless steel.

Supports: Legs or base.

Controls.

Thermometer: Control panel or tank rim mounted.

Supply: Over-the-rim fill spout.

Drain(s): One or two waste connections.

Electric Turbine Ejectors: Two; one rail mounted on each side.

Thermostatic mixing-valve assembly.

Unit Electrical Characteristics:

Volts: [120] [240] [277] [480] <Insert number>.

Phase(s): [One] [Three].

Hertz: [60] <Insert number>.

Full-Load Amperes: <Insert value>.

Minimum Circuit Ampacity: <Insert value>.

Maximum Overcurrent Protection: <Insert amperage>.

Insert or delete optional features below to suit Project. Many are available.

Hose and hand-held shower.

Wash-out-hose assembly.

Stretcher lift.

Overhead[ electric] hoist.

<Insert option>.

Copy "Hydrotherapy Whirlpools" Paragraph below and re-edit for each type of full-body, immersion-tank hydrotherapy whirlpool required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each hydrotherapy whirlpool.

Hydrotherapy Whirlpools <Insert drawing designation>: Full-body immersion tank.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

ARJO, Inc.

Ferno Ille.

Whitehall Manufacturing.

<Insert Manufacturer's name>.

Description: Stationary rectangular tank for full-body massage.

Tank Dimensions: [90 by 32 by 19 inches (2286 by 813 by 483 mm)] [95 by 41 by 22 inches (2413 by 1041 by 560 mm)] <Insert dimensions>.

Overall Height: 32 or 34 inches (813 or 860 mm).

Water Capacity: [195 gal. (738 L)] [260 gal. (984 L)] <Insert value>.

Material: Stainless steel.

Supports: Legs or base.

Controls.

Thermometer: Control panel or tank rim mounted.

Supply: Over-the-rim fill spout.

Drain(s): One or two waste connections.

Electric Turbine Ejector: One, tank mounted [at end] [on rail] [on side].

Thermostatic mixing-valve assembly.

Unit Electrical Characteristics:

Volts: [120] [240] [277] [480] <Insert number>.

Phase(s): [One] [Three].

Hertz: [60] <Insert number>.

Full-Load Amperes: <Insert value>.

Minimum Circuit Ampacity: <Insert value>.

Maximum Overcurrent Protection: <Insert amperage>.

Insert or delete optional features below to suit Project. Many are available.

Hose and hand-held shower.

Wash-out-hose assembly.

Stretcher lift.

Overhead[ electric] hoist.

<Insert option>.

HOSE BOXES

Caution: Authorities having jurisdiction may require backflow preventers in water-supply piping or on hose-thread outlets.

Copy "Hose Boxes" Paragraph below and re-edit for each type of hose box required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each hose box.

Hose Boxes <Insert drawing designation>: For utility equipment.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Basis-of-Design Product: Subject to compliance with requirements, provide Willoughby Industries; [HB-8140] [HB-8141] [HB-8145] [HB-8146] [HB-8150] [HB-8151] [HB-8155] [HB-8156] [HB-8180] [HB-8181] [HB-8185] or comparable product by one of the following:

Bradley Corporation.

<Insert Manufacturer's name>.

Description: Recess-mounted outlet box with water-supply and optional drain connections.

Box and Faceplate: Stainless steel.

Supply Fitting(s): [One] [Two] NPS 1/2 (DN 15) Brass valve(s) and adapter with male hose-thread outlet.

Drain: [Yes] [No] NPS 2 (DN 50) standpipe, P-trap, and direct waste connection to drainage piping.

Door: [Yes] [No] Stainless steel hinged with lock.

Vacuum Breaker: [Yes] [No].

Reinforcement: Fire-retardant-treated wood blocking between studs. Comply with fire-retardant-treated wood requirements specified in Section 061000 "Rough Carpentry."

DIALYSIS BOXES

Caution: Authorities having jurisdiction may require backflow preventers in water-supply piping or on hose-thread outlets.

Copy "Dialysis Boxes" Paragraph below and re-edit for each type of dialysis equipment outlet box required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each dialysis box.

Dialysis Boxes: <Insert drawing designation>: For dialysis equipment.

Basis-of-Design Product: Subject to compliance with requirements, provide Willoughby Industries; [DB-8190] [DB-8191] [DB-8195] [DB-8196] or a comparable product by one of the following:

Bradley Corporation.

Metcraft Industries, Inc.

<Insert manufacturer's name>.

Description: Recessed-mounted outlet box with water-supply and drain connections.

Box and Faceplate: Type 316 stainless steel.

Add "Box Dimensions" subparagraph below if required.

Supply Fitting(s): [One] [Two] NPS 1/2 (DN 15) PVC ball valve(s) and adapter with male lose-thread outlet.

Trap optional or to be supplied by contractor.

Drain: NPS 2 (DN 50) No hub standpipe, P-trap, and direct waste connection to drainage piping.

Reinforcement: Fire-retardant-treated wood blocking between studs. Comply with fire-retardant-treated wood requirements specified in Section 061000 "Rough Carpentry".

BEHAVIORAL HEALTH CARE LAVATORY

Caution, these fixtures require a trap with waste and vent connections for installation in the base and vertical vent piping through top of unit, or they may be installed with a trap and vent under the floor below the fixture.

Copy "Behavioral Health Care Lavatory" Paragraph below and re-edit for each type of Behavioral Health Care Lavatory required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each Behavioral Health Car Lavatory.

Behavioral Health Care Lavatory <Insert drawing designation>: Wall Mounted, Solid Surface Ligature-Resistant Lavatory System.

Basis-of-Design Product: Subject to compliance with requirements, provide Willoughby Industries; WBL-2320 or a comparable product by one of the following:

Odd Ball Industries.

<Insert manufacturer's name>.

Standard: CSA B45.5/IAPMO Z124.

Ligature-Resistant Lavatory Basic:

Standard: CSA B45.5/IAPMO Z124.

Material: Solid Surface.

For color options, refer to Willoughby Industries website at http://www.willoughby-ind.com/Portals/0/Marketing/Aquasurf-Color-Chart.pdf

Color or Finish: <Insert color from manufacturer's full selection>.

Nominal Size: 23 by 20 inches (584 by 508 mm).

Retain first option in "Height to Rim" subparagraph below for adult height receptors. Retain the second option for child height receptors.

Height to Rim: [34 inches (864 mm)] [31 inches (787 mm)] above floor.

Drain: Ligature-resistant machined stainless steel with NPS 1-1/4 (DN 32).

Spray Head:

Material: Machined type 303 stainless steel base with spray nozzle.

Spray: Non-aerated laminar spray.

Spray Nozzles: Complying with NSF 61, NSF/ANSI 372, and ASME A112.18.1/CSA B125.1.

Verify option retained in "Control" subparagraph below is available from listed manufacturer's and for type of lavatory required.

Control: [Individual pneumatic push-button] [Individual electronic pushbutton] [Individual piezo-electric pushbutton] [Individual hardwired IR sensor] [Individual battery-powered IR sensor].

Pedestal:

Wall Mounted.

Stainless steel with access panel.

For color options, refer to Willoughby Industries website at http://www.willoughby-ind.com/Portals/0/Marketing/Starboard Color Chart.pdf

Solid polymer side panels: <Insert color from manufacturer's full selection>.

Supply Fittings:

Piping: NPS 1/2 (DN 15) FIP.

Valves: Shutoff on valve supply.

Supply piping: From wall.

Waste Fittings:

Standard: ASME A112.18.2/CSA B125.2

Trap optional or to be supplied by contractor.

Trap and Drain Piping: NPS 1-1/4 (DN 32) tailpieces.

Behavioral Health Care Lavatory <Insert drawing designation>: Stainless Steel, Ligature-Resistant Lavatory System, Wall Mounted, Rear Mounted.

Basis-of-Design Product: Subject to compliance with requirements, provide Willoughby Industries; WBLS-2018-HC or a comparable product by one of the following:

Bradley Corporation.

<Insert manufacturer's name>.

Standard: CSA B45.5/IAPMO Z124.

Construction:

Standard: CSA B45.5/IAPMO Z124.

Material: Fabricated from 14 gauge, type 304 stainless steel.

Finish: Exposed stainless surfaces polished to a #4 satin finish.

Nominal Size: 17.5 inches by 20.125 inches (446 mm by 511 mm).

Retain first option in "Height to Rim" subparagraph below for adult height receptors. Retain the second option for child height receptors.

Height to Rim: [34 inches (854 mm)] [31 inches (787 mm)] above floor.

Drain: Integral slow drain.

Bubbler/Filler:

Material: Machined from type 303 stainless steel.

Verify option retained in "Control" subparagraph below is available from listed manufacturer's and for type of lavatory required.

Control: Ligature-resistant [Single temperature pneumatic metering push-button] [Dual temperature pneumatic metering push-button] [Single temperature electronic metering pushbutton] [Dual temperature electronic metering pushbutton] [Single temperature piezo-electric metering pushbutton] [Dual temperature piezo-electric metering pushbutton].

Supply Fittings:

Standard: ASME A112.18.1/CSA B125.1.

Piping: NPS 1/2 (DN 15) FIP.

Valves: Shutoff on valve supply.

Supply Piping: From wall.

Waste Fittings:

Standard: ASME A112.18.2/CSA B125.2.

Waste: NPS 1-1/2 (DN 40) FIP elbow waste connection.

Trap optional or to be supplied by contractor.

Trap: Option LW1, [Yes] [No].

Accessories:

Towel Hooks: [One] [Two] on [Both] [Left] [Right] side(s) of fixture.

Mounting:

Mounting Hardware: 1/2-13 all thread rods with washers and nuts. Unit requires chase for installation.

Optional Wall Sleeve: [Yes] [No] Galvanized-steel frame of dimensions required to match fixture. Include steel bars or other design to prevent escape if fixture is removed.

Color: WHITE [Yes] [No].

Behavioral Health Care Lavatory <Insert drawing designation>: Stainless Steel, Ligature-Resistant Lavatory System, Wall Mounted, Front Mounted.

Basis-of-Design Product: Subject to compliance with requirements, provide Willoughby Industries; WBLS-2018-HC-FA or a comparable product by one of the following:

Bradley Corporation.

<Insert manufacturer's name>.

Standard: CSA B45.5/IAPMO Z124.

Construction:

Standard: CSA B45.5/IAPMO Z124.

Material: Fabricated from 14 gauge, type 304 stainless steel.

Finish: Exposed stainless surfaces polished to a #4 satin finish.

Nominal Size: 17.5 inches by 20.125 inches (446 mm by 511 mm).

Retain first option in "Height to Rim" subparagraph below for adult height receptors. Retain the second option for child height receptors.

Height to Rim: [34 inches (854 mm)] [31 inches (787 mm)] above floor.

Drain: Integral slow drain.

Bubbler/Filler:

Material: Machined from type 303 stainless steel.

Verify option retained in "Control" subparagraph below is available from listed manufacturer's and for type of lavatory required.

Control: Ligature-resistant [Single temperature pneumatic metering push-button] [Dual temperature pneumatic metering push-button] [Single temperature electronic metering pushbutton] [Dual temperature electronic metering pushbutton] [Single temperature piezo-electric metering pushbutton] [Dual temperature piezo-electric metering pushbutton].

Supply Fittings:

Standard: ASME A112.18.1/CSA B125.1.

Piping: NPS 1/2 (DN 15) FIP.

Valves: Shutoff on valve supply.

Supply Piping: From wall.

Waste Fittings:

Standard: ASME A112.18.2/CSA B125.2.

Waste: NPS 1-1/2 (DN 40) FIP.

Trap optional or to be supplied by contractor.

Trap: RPT.

Accessories:

Towel Hooks: [One] [Two] on [Both] [Left] [Right] side(s) of fixture.

Mounting:

Mounting: From front, Anchoring holes provided.  No chase required.

Color: WHITE [Yes] [No].

Behavioral Health Care Lavatory <Insert drawing designation>: Stainless Steel, Ligature-Resistant Lavatory System, Floor Mounted, Rear Mounted.

Basis-of-Design Product: Subject to compliance with requirements, provide Willoughby Industries; ASHS-1013-06 or a comparable product by one of the following:

Bradley Corporation.

<Insert manufacturer's name>.

Standard: CSA B45.5/IAPMO Z124.

Construction:

Standard: CSA B45.5/IAPMO Z124.

Material: Fabricated from 14 gauge, type 304 stainless steel.

Finish: Exposed stainless surfaces polished to a #4 satin finish.

Nominal Size: 18 inches by 14 inches (457 mm by 356 mm).

Height to Rim: 34 inches (854 mm) above floor.

Drain: Integral slow drain.

Bubbler/Filler:

Material: Machined from type 303 stainless steel.

Verify option retained in "Control" subparagraph below is available from listed manufacturer's and for type of lavatory required.

Control: Ligature-resistant [Single temperature pneumatic metering push-button] [Dual temperature pneumatic metering push-button] [Single temperature electronic metering pushbutton] [Dual temperature electronic metering pushbutton] [Single temperature piezo-electric metering pushbutton] [Dual temperature piezo-electric metering pushbutton].

Supply Fittings:

Standard: ASME A112.18.1/CSA B125.1.

Piping: NPS 1/2 (DN 15) FIP.

Valves: Shutoff on valve supply.

Supply Piping: From wall.

Waste Fittings:

Standard: ASME A112.18.2/CSA B125.2.

Waste: NPS 1-1/2 (DN 40) FIP elbow waste connection.

Trap optional or to be supplied by contractor.

Trap: Option LW1, [Yes] [No].

Accessories:

Towel Hooks: [One] [Two] on [Both] [Left] [Right] side(s) of fixture.

Mounting:

Mounting Hardware: 1/2-13 all thread rods with washers and nuts. Unit requires chase for installation.

Optional Wall Sleeve: [Yes] [No] Galvanized-steel frame of dimensions required to match fixture. Include steel bars or other design to prevent escape if fixture is removed.

Behavioral Health Care Lavatory <Insert drawing designation>: Stainless Steel, Ligature-Resistant Lavatory System, Floor Mounted, Front Access.

Basis-of-Design Product: Subject to compliance with requirements, provide Willoughby Industries; ASHS-1013-06-FA or a comparable product by one of the following:

Bradley Corporation.

<Insert manufacturer's name>.

Standard: CSA B45.5/IAPMO Z124.

Construction:

Standard: CSA B45.5/IAPMO Z124.

Material: Fabricated from 14 gauge, type 304 stainless steel.

Finish: Exposed stainless surfaces polished to a #4 satin finish.

Nominal Size: 18 inches by 14 inches (457 mm by 356 mm).

Height to Rim: 34 inches (854 mm) above floor.

Removable access panels.

Drain: Integral slow drain.

Bubbler/Filler:

Material: Machined from type 303 stainless steel.

Verify option retained in "Control" subparagraph below is available from listed manufacturer's and for type of lavatory required.

Control: Ligature-resistant [Single temperature pneumatic metering push-button] [Dual temperature pneumatic metering push-button] [Single temperature electronic metering pushbutton] [Dual temperature electronic metering pushbutton] [Single temperature piezo-electric metering pushbutton] [Dual temperature piezo-electric metering pushbutton].

Supply Fittings:

Standard: ASME A112.18.1/CSA B125.1.

Piping: NPS 1/2 (DN 15) FIP.

Valves: Shutoff on valve supply.

Supply Piping: From wall.

Waste Fittings:

Standard: ASME A112.18.2/CSA B125.2.

Waste: NPS 1-1/2 (DN 40) FIP removable "P" trap.

Accessories:

Towel Hooks: [One] [Two] on [Both] [Left] [Right] side(s) of fixture.

Mounting:

Mounting Hardware: From the front through anchoring holes. Unit requires no chase for installation and maintenance.

BARIATRIC HEALTH CARE LAVATORY

Caution, these fixtures require a trap with waste and vent connections for installation in the base and vertical vent piping through top of unit, or they may be installed with trap and vent under the floor below the fixture.

Copy "Bariatric Health Care Lavatory" Paragraph below and re-edit for each type of lavatory required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each bariatric health care lavatory.

Bariatric Health Care Lavatory <Insert drawing designation>: Solid-surface, Floor Mounted Lavatory System.

Basis-of-Design Product: Subject to compliance with requirements, provide Willoughby Industries; BHS-3123 or a comparable product by one of the following:

<Insert manufacturer's name>.

Standard: CSA B45.5/IAPMO Z124, CSA Z8000, Facility Guides Institute.

Load Rating: Minimum 1000 lbs (454 kg) vertical static load.

Bariatric Lavatory basin:

Standard: CSA B45.5/IAPMO Z124.

Material: Solid surface.

For color options, refer to Willoughby Industries website at http://www.willoughby-ind.com/Portals/0/Marketing/Aquasurf Color Chart.pdf

Color of Finish: <Insert color from manufacturer's full selection>.

Nominal Size: 31 by 23 inches (787 by 584 mm).

Height to Rim: 34 inches (864 mm) above floor.

Drain: Anti-Microbial with NPS 1-1/4 (DN 32) tail piece.

Faucet:

Standard: ASME A112.18.1/CSA B125.1.

Type: Deck Mounted 4 inch (102 mm) CC, 8 inch (203 mm) gooseneck, 1.5 gpm (0.09 L/s) Laminar Flow, [With wrist blades] [Infrared hard wired] [Infrared battery operated].

Pedestal:

Mounting: Floor mounted.

Material: Heavy gauge stainless steel.

For Solid Polymer Panel color options, refer to Willoughby Industries website at http://www.willoughby-ind.com/Portals/0/Marketing/Starboard Color Chart.pdf

For Wood Grain Panel color options, refer to Willoughby Industries website at http://www.willoughby-ind.com/Portals/0/Marketing/WoodGrain Color Chart.pdf

Solid polymer side panels: [Solid Polymer <Insert color from manufacturer's full selection>] [Wood Grain <Insert wood grain color from manufacturer's full selection>].

Supply Fittings:

Standard: ASME A112.18.1/CSA B125.1.

Piping: NPS 3/8 (DN 10) FIP.

Supply Piping: From wall.

Waste Fittings:

Standard: ASME A112.18.2/CSA B125.2.

Anti-microbial trap optional or to be supplied by contractor.

Trap and Drain Piping: NPS 1-1/4 (DN 32) tailpiece.

INFECTION CONTROL SINK

Copy "Infection Control Sink" Paragraph below and re-edit for each type of Infection Control Sink required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify each Infection Control Sink.

Infection Control Sink <Insert drawing designation>: Solid Surface, Wall Mounted Sink.

Basis-of-Design Product: Subject to compliance with requirements, provide Willoughby Industries; WICS-2222 or a comparable product by one of the following:

Sloan Valve Company.

<Insert manufacturer's name>.

Standard: CSA B45.5/IAPMO Z124, Z8000, Facility Guides Institute.

Infection Control Sink Basin:

Standard: CSA B45.5/IAPMO Z124.

Material: Anti-microbial solid surface.

Drain: Offset.

Integral side and rear splash-guards.

For Solid Polymer Panel color options, refer to Willoughby Industries website at http://www.willoughby-ind.com/Portals/0/Marketing/Aquasurf-Color-Chart.pdf

Color: <Insert color from manufacturer's full selection>.

Nominal Size: 22 by 22 inches (559 by 559 mm).

Retain first option in "Height to Rim" subparagraph below for adult height receptors. Retain the second option for child height receptors.

Height to Rim: [34 inches (854 mm)] [31 inches (787 mm)] above floor.

Drain: Anti-microbial with NPS 1-1/4 (DN 32) tail piece.

Faucet:

Standard: ASME A112.18.1/CSA B125.1.

Type: Deck Mounted, 4 inch (102 mm) CC, 3-1/2 inch (89 mm) Rigid gooseneck, 1.5 gpm, (0.09 L/s) Laminar flow, [Infrared hard wired] [Infrared battery operated].

Pedestal:

Wall mounted.

Stainless Steel.

Polished stainless steel trap shroud.

Supply Fittings:

Piping: NPS 3/8 (DN 10) FIP.

Valves: Shutoff on wall.

Supply Piping: From wall.

Waste Fittings:

Standard: ASME A112.18.2/CSA B125.2.

Anti-microbial trap optional or to be supplied by contractor.

Drain: NPS 1-1/4 (DN 32) tailpiece.

MORGUE EQUIPMENT

Willoughby Industries does not manufacture Morgue Equipment.

Equipment in this article is typically custom made. Consult user or manufacturer's representative before equipment and option selection.

Copy "Autopsy Table" Paragraph below and re-edit for each type of autopsy table required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify morgue equipment.

Autopsy Table <Insert drawing designation>:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

CSI Industries Inc.

LEEC International, Inc.

Thermo Fisher Scientific, Inc.

<Insert Manufacturer's name>.

Description: Pedestal stainless-steel table with sink; designed for downdraft ventilation.

Material: Stainless steel.

Nominal Size: [88 by 30 inches (2250 by 762 mm)] <Insert dimensions> with deck faucet holes.

Faucet: Manufacturer's standard, deck mounted with wrist- or elbow-blade handles.

Aspirator: Deck mounted.

Removable body supports.

Rinse Assembly: Deck-mounted faucet with hose.

Disposer: [Not required] [Required, according to UL 430].

Receptacle: Duplex, hospital grade with ground-fault interruption.

Supplies: With atmospheric vacuum breakers, according to ASSE 1001, and stops.

Drain: [Grid] <Insert type> with NPS 1-1/2 (DN 40) tailpiece.

Waste piping.

Unit Electrical Characteristics:

Volts: [120] [240] [277] [480] <Insert number>.

Phase(s): [One] [Three].

Hertz: [60] <Insert number>.

Full-Load Amperes: <Insert value>.

Minimum Circuit Ampacity: <Insert value>.

Maximum Overcurrent Protection: <Insert amperage>.

Copy "Dissecting Sink" Paragraph below and re-edit for each type of dissecting sink required.

Insert letter and number combination to complete drawing designation. Use these designations on Drawings to identify morgue equipment.

Dissecting Sink <Insert drawing designation>:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

CSI Industries Inc.

LEEC International, Inc.

Thermo Fisher Scientific, Inc.

<Insert Manufacturer's name>.

Description: Wall-mounted sink with backsplash.

Material: Stainless steel.

Nominal Size: [84 by 28 inches (2130 by 710 mm)] <Insert dimensions> with back faucet holes.

Nominal Size: Approximately 30 inches (760 mm) wide.

Equipment drawer.

Coordinate "Faucet" Subparagraph with "Sink Faucets" Article.

Faucet: <Insert faucet designation>.

Aspirator: Back mounted.

Rinse Assembly: One back-mounted faucet with hose.

Disposer: [Not required] [Required, according to UL 430].

Support: ASME A112.6.1M, Type I or Type III sink carrier.

Supplies: With atmospheric vacuum breakers, according to ASSE 1001, and stops.

Drain: [Grid] <Insert type> with NPS 1-1/2 (DN 40) tailpiece.

Waste Piping: Comply with requirements in "Waste Fittings" Article.

Back-mounted, hand-held-type eye wash.

Unit Electrical Characteristics:

Volts: [120] [240] [277] [480] <Insert number>.

Phase(s): [One] [Three].

Hertz: [60] <Insert number>.

Full-Load Amperes: <Insert value>.

Minimum Circuit Ampacity: <Insert value>.

Maximum Overcurrent Protection: <Insert amperage>.

SUPPLY FITTINGS

NSF Standard: Comply with NSF 61 Annex G, "Drinking Water System Components - Health Effects," for supply-fitting materials that will be in contact with potable water.

Standard: ASME A112.18.1/CSA B125.1.

Supply Piping: Chrome-plated brass pipe or chrome-plated copper tube matching water-supply piping size. Include chrome-plated brass or stainless-steel wall flange.

Supply Stops: Chrome-plated brass, one-quarter-turn, ball-type or compression valve with inlet connection matching supply piping.

Retain "Wheel handle" option in "Operation" Paragraph below for one-quarter-turn, ball-type stops.

Operation: [Loose key] [Wheel handle] <Insert type>.

Risers: NPS 1/2 (DN 15) [chrome-plated, rigid-copper pipe and brass straight or offset tailpieces] [chrome-plated, soft-copper flexible tube] [ASME A112.18.6, braided or corrugated stainless-steel, flexible hose].

WASTE FITTINGS

Standard: ASME A112.18.2/CSA B125.2.

Drain: [Grid] <Insert type> with NPS 1-1/2 DN 40 tailpiece.

Trap:

Size: NPS 1-1/2 (DN 40).

Retain one of two "Material" subparagraphs below.

Material: Chrome-plated, [two-piece, cast-brass trap and swivel elbow with 0.032-inch- (0.83-mm-) thick brass tube to wall] [two-piece, cast-brass trap and ground-joint swivel elbow with 0.032-inch- (0.83-mm-) thick brass tube to wall] [one-piece, cast-brass trap with swivel 0.029-inch- (73-mm-) thick tubular brass wall bend] <Insert trap type>; and chrome-plated brass or steel wall flange.

Material: Stainless-steel, two-piece trap and swivel elbow with 0.012-inch- (0.30-mm-) thick stainless-steel tube to wall; and stainless-steel wall flange.

GROUT

Standard: ASTM C 1107/C 1107M, Grade B, post-hardening and volume-adjusting, dry, hydraulic-cement grout.

Characteristics: Nonshrink; recommended for interior and exterior applications.

Design Mix: 5000-psi (34.5-MPa), 28-day compressive strength.

Packaging: Premixed and factory packaged.

EXECUTION

EXAMINATION

Examine roughing-in of water-supply and sanitary drainage and vent piping systems to verify actual locations of piping connections before fixture installation.

Examine walls, floors, cabinets, and counters for suitable conditions where fixtures will be installed.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSTALLATION

Install healthcare plumbing fixtures level and plumb according to roughing-in drawings.

Install supports, affixed to building substrate, for wall-mounted fixtures.

Use carrier supports with waste fitting and seal for back-outlet fixtures.

Use carrier supports without waste fitting for fixtures with tubular waste piping.

Use chair-type carrier supports with rectangular steel uprights for accessible fixtures.

Install floor-mounted healthcare water closets on bowl-to-drain, connecting fitting attachments to piping or building substrate.

First paragraph below applies to counter-mounted fixtures such as sinks.

Install counter-mounted fixtures in and attached to casework.

Install water-supply piping with stop on each supply to each fixture to be connected to water-distribution piping. Attach supplies to supports or substrate within pipe spaces behind fixtures. Install stops in locations where they can be easily reached for operation.

Exception: Use ball or gate valve if supply stops are not specified with fixture. Comply with valve requirements specified in Section 220523.12 "Ball Valves for Plumbing Piping" and Section 220523.15 "Gate Valves for Plumbing Piping."

Install flushometer valves on healthcare water closets.

Install flushometer valves for accessible healthcare water closets, with lever handle mounted on wide side of compartment.

Install toilet seats on healthcare water closets.

Install faucet flow-control fittings with specified flow rates and patterns in faucet spouts, if faucets are not available with required rates and patterns. Include adapters if required.

Install laminar-flow, faucet-spout fittings in faucet spouts where laminar-flow fittings are specified.

Install shower flow-control fittings with specified maximum flow rates in shower arms.

Install traps on fixture outlets.

Exception: Omit trap on fixtures with integral traps.

Set healthcare showers in leveling bed of cement grout.

Coordinate first paragraph below with Drawings. Indicate on Drawings those fixtures and sinks that are required to be accessible.

Install protective shielding pipe covers and enclosures on exposed supplies and waste piping of accessible sinks. Comply with requirements in Section 220719 "Plumbing Piping Insulation."

Seal joints between healthcare plumbing fixtures, counters, floors, and walls using sanitary-type, one-part, mildew-resistant silicone sealant. Match sealant color to fixture color. Comply with sealant requirements specified in Section 079200 "Joint Sealants."

Install wall flanges or escutcheons at piping wall penetrations in exposed, finished locations. Use deep-pattern escutcheons if required to conceal protruding fittings. Comply with escutcheon requirements specified in Section 220518 "Escutcheons for Plumbing Piping."

CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

Connect fixtures with water supplies, stops, and risers, and with traps, soil, waste, and vent piping. Use size fittings required to match fixtures.

Comply with requirements for water piping specified in Section 221116 "Domestic Water Piping."

Comply with requirements for soil and waste drainage piping[ and vent piping] specified in Section 221316 "Sanitary Waste and Vent Piping."

Comply with requirements for atmospheric vent piping specified in Section 221316 "Sanitary Waste and Vent Piping."

Install protective shielding pipe covers and enclosures on exposed supplies and waste piping of accessible sinks. Comply with requirements in Section 220719 "Plumbing Piping Insulation."

ADJUSTING

Operate and adjust faucets and controls. Replace damaged and malfunctioning healthcare plumbing fixtures, fittings, and controls.

Adjust water pressure at [faucets] [and] [flushometer valves] to produce proper flow.

Install fresh batteries in battery-powered, electronic-sensor mechanisms.

CLEANING AND PROTECTION

After installing healthcare plumbing fixtures, inspect and repair damaged finishes.

Clean healthcare plumbing fixtures, faucets, and other fittings with manufacturers' recommended cleaning methods and materials.

Provide protective covering for installed fixtures and fittings.

Do not allow use of healthcare plumbing fixtures for temporary facilities unless approved in writing by Owner.

END OF SECTION 224300